LIGO Sensor 2.1.8

RS485 Protocol Reference

Reverse-engineered from serial captures  |  Build 201204  |  Serial ID: 77DFEC5D

# 1. Frame Format

All commands from the PC configurator to the sensor follow this fixed frame structure:

| Byte 0 | Byte 1 | Byte 2 | Byte 3 | Byte 4 | Notes |
| --- | --- | --- | --- | --- | --- |
| 0xB0 | REG lo | 0xFF | VALUE | 0x00 | Terminator |
| Command | Register ID | Always FF | Encoded value | Always 00 | 4 or 5 bytes total |

The 0xFF high byte is constant across all register addresses observed. Register space is therefore entirely within the 0xFF00–0xFFFF range.

Frames are either 4 bytes (val=0x00, terminator only) or 5 bytes (val + 0x00 terminator).

Baud rate: 9600. Interface: RS485 half-duplex.

# 2. Protocol Flow — Config Write Sequence

When saving config from the PC configurator, the protocol follows a strict write-then-verify pattern:

- PC sends factory reset command: {B0}{DB}{FF}{00}

- PC sends one register write command: {B0}{REG}{FF}{VAL}{00}

- PC sends factory reset again (inter-write reset/apply)

- Steps 2–3 repeat for each config register

- Sensor responds with a 47-byte live data frame after the sequence

The factory reset command (0xFFDB) appears between every register write. This may act as a 'commit/apply' trigger in the firmware between writes, rather than a true full reset each time.

# 3. Confirmed Commands

The following commands have been confirmed by direct capture and cross-reference with UI actions:

| Raw bytes | Register | Command / field | Value / meaning | Status |
| --- | --- | --- | --- | --- |
| B0 DB FF 00 | 0xFFDB | Factory reset | val=0x00 — triggers full reset | Confirmed |
| B0 DB FF 00 B0 EF FF 00 | 0xFFEF | Set empty (0 mm reference) | val=0x00 — mark current as zero | Confirmed |
| B0 DB FF 00 B0 ED FF xx 00 | 0xFFED | Set full (max mm reference) | val=raw OSC snapshot at fill level | Confirmed |
| B0 E5 FF 01 00 | 0xFFE5 | Device address (0–254) | val=address (e.g. 0x01 = addr 1) | Confirmed |

Set empty sequence: factory reset (0xFFDB) always precedes 0xFFEF to clear previous calibration offset before marking the new zero point.

Set full value: the val byte in 0xFFED is NOT fixed — it encodes the raw OSC/ADC reading at the moment Set full is triggered. Example captured: val=0x77 (119) at fuel height 2.7 mm.

# 4. Config Write Registers

These registers are written during a Save Config → To Sensor operation. Values are encoded (not direct decimal) — encoding formula not yet fully reverse-engineered:

| Raw bytes | Register | Config field | Captured val | UI setting |
| --- | --- | --- | --- | --- |
| B0 B5 FF 00 | 0xFFB5 | Level min voltage | 0x00 = 0 | Level min = 0 V (1.0–8.0 V range) |
| B0 F9 FF 00 | 0xFFF9 | Level max voltage | 0x00 → 5 V | Level max = 5 V (2.0–9.0 V range) |
| B0 DD FF 00 | 0xFFDD | Output type | 0x00 = Analog | Output type = Analog |
| B0 D9 FF 61 00 | 0xFFD9 | Filter time | 0x61 = 97 | Filter time = 1 s (encoded) |
| B0 D1 FF 17 00 | 0xFFD1 | Message interval | 0x17 = 23 | Message interval = 1 s (encoded) |
| B0 E3 FF AB 00 | 0xFFE3 | Autocalib feature | 0xAB = 171 | Autocalib = Enable (encoded) |
| B0 EB FF DD 00 | 0xFFEB | Unknown | 0xDD = 221 | Unknown — possibly length lo byte |
| B0 B1 FF 4D 00 | 0xFFB1 | Unknown | 0x4D = 77 | Unknown — possibly length hi byte |
| B0 95 FF B7 00 | 0xFF95 | Unknown | 0xB7 = 183 | Unknown — possibly auto-calib ref |

Registers 0xFFEB and 0xFFB1 likely encode the Actual Length (mm) parameter as a 16-bit split value, but the encoding does not match a simple little-endian representation of 750 (0x02EE).

Filter time (0xFFD9) and Message interval (0xFFD1) captured values (0x61=97, 0x17=23) do not match the UI value of 1s directly — a scaling or offset formula applies.

# 5. Sensor Response Frame (47 bytes)

The sensor transmits a 47-byte live data frame in response to read requests. All values are little-endian 16-bit words. 0xFFFF bytes indicate unimplemented/unused registers (EEPROM default fill value):

Example captured frame:

B0 B9 DB FF DB FF FF F7 14 74 72 4E FF F9 39 FF FF E1 FF FF FF FF FF FF FF FF FF FF FF FF FF FF FF C5 FF C5 FF C5 FF FF FF FF FF FF FF 85 00

| Bytes | Field | Raw value | Displayed value |
| --- | --- | --- | --- |
| 0–1 | Header / preamble | 0xB0 0xB9 | Frame start identifier |
| 2–3 | OSC frequency | 0xFFDB (LE word) | 25372 — processed by firmware formula |
| 4–5 | OSC frequency (repeat) | 0xFFDB | Second measurement / redundancy |
| 6–7 | Status / flags | 0xF7FF bitmask | Sensor status bits |
| 8–9 | Level output (0–4095) | 0x7414 = 29716 | 15 — scaled via level min/max settings |
| 10–11 | Fuel height (mm) | 0x4E72 = 20082 | 2.7 mm — derived from level ÷ length × cal. |
| 12–13 | Fuel volume (liter) | 0xF9FF | 0 — requires calibration table |
| 14–15 | Voltage out (mV) | 0xFF39 | 0 — analog output (RS485 = 0) |
| 16–17 | Sensor temperature | 0xE1FF signed | 18 °C — offset corrected |
| 18–43 | Padding / unused registers | 0xFFFF × 26 | Unimplemented registers (EEPROM default) |
| 28,30,32 | Sensor message sentinel | 0xFFC5 × 3 | "None" — no error condition |
| 44–45 | CRC / checksum | 0x0085 0x00 | Frame integrity check |

# 6. Register Address Map

Complete register map in ascending address order. All registers are in the 0xFF__ space:

| Register | Field / command | Category |
| --- | --- | --- |
| 0xFF95 | Unknown (possibly autocalib ref) | Config write — unknown |
| 0xFFB1 | Unknown (possibly actual length hi) | Config write — unknown |
| 0xFFB5 | Level min voltage | Config write — confirmed |
| 0xFFD1 | Message interval | Config write — confirmed |
| 0xFFD9 | Filter time | Config write — confirmed |
| 0xFFDB | Factory reset | Control command — confirmed |
| 0xFFDD | Output type | Config write — confirmed |
| 0xFFE3 | Autocalib feature | Config write — confirmed |
| 0xFFE5 | Device address (0–254) | Config write — confirmed |
| 0xFFEB | Unknown (possibly actual length lo) | Config write — unknown |
| 0xFFED | Set full (max mm reference) | Calibration command — confirmed |
| 0xFFEF | Set empty (0 mm reference) | Calibration command — confirmed |
| 0xFFF9 | Level max voltage | Config write — confirmed |

# 7. Device Information

Captured from the Info device panel of the configurator:

| Parameter | Value |
| --- | --- |
| FW version | 2.4.12 |
| HW version | LGS86:OP:1.3 |
| Boot version | S8:02:00 |
| Serial ID | 77DFEC5D |
| COM Port | COM13 |
| Baud rate | 9600 |
| Sensor type | RS485 |
| Address | 1 |
| Actual length | 750 mm |

# 8. Open Questions / Still to Capture

- Actual length encoding — change length value and re-capture to decode 0xFFEB / 0xFFB1

- Filter time / message interval formula — test with different values to find scale factor

- Set full value formula — capture at a known fill height to decode the OSC snapshot encoding

- Change password command — likely near 0xFFE3–0xFFE5 register range

- Update firmware sequence — likely a multi-byte or special-framed protocol

- Prefix / Postfix string registers — not yet observed in captures

- Automatic transmission ON mode — capture to find interval/trigger register